## Jan-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
EFFLUENT HARDNESS / MG/L
January | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 430 | 135
2 | 433 | 138
3 | 457 | 146
4 | 495 | 149
5 | 490 | 146
6 | 470 | 140
7 | 470 | 126
8 | 470 | 144
9 | 460 | 137
10 | 460 | 142
11 | 463 | 147
12 | 470 | 143
13 | 470 | 143
14 | 488 | 155
15 | 476 | 142
16 | 463 | 141
17 | 431 | 131
18 | 453 | 139
19 | 423 | 143
20 | 420 | 137
21 | 427 | 138
22 | 423 | 137
23 | 405 | 131
24 | 455 | 139
25 | 540 | 148
26 | 534 | 141
27 | 466 | 132
28 | 416 | 133
29 | 408 | 132
30 | 426 | 140
31 | 448 | 146
AVERAGE | 456.129 | 140.0323
MAX | 540 | 155
MIN | 405 | 126

## Feb-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
EFFLUENT HARDNESS / MG/L
February | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 440 | 139
2 | 435 | 142
3 | 430 | 134
4 | 443 | 142
5 | 440 | 140
6 | 445 | 142
7 | 480 | 146
8 | 453 | 143
9 | 465 | 145
10 | 470 | 143
11 | 460 | 140
12 | 442 | 142
13 | 460 | 143
14 | 470 | 148
15 | 468 | 143
16 | 467 | 145
17 | 468 | 140
18 | 453 | 130
19 | 453 | 144
20 | 450 | 145
21 | 433 | 137
22 | 435 | 142
23 | 420 | 138
24 | 382 | 128
25 | 400 | 138
26 | 412 | 149
27 | 382 | 144
28 | 386 | 146
AVERAGE | 440.7857 | 141.3571
MAX | 480 | 149
MIN | 382 | 128

## Mar-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
EFFLUENT HARDNESS / MG/L
March | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 380 | 141
2 | 365 | 137
3 | 330 | 141
4 | 350 | 148
5 | 365 | 140
6 | 355 | 143
7 | 355 | 141
8 | 383 | 148
9 | 428 | 145
10 | 418 | 133
11 | 443 | 149
12 | 441 | 141
13 | 402 | 140
14 | 443 | 145
15 | 473 | 151
16 | 456 | 141
17 | 437 | 141
18 | 403 | 130
19 | 380 | 137
20 | 370 | 140
21 | 361 | 136
22 | 390 | 144
23 | 380 | 136
24 | 388 | 144
25 | 382 | 138
26 | 408 | 146
27 | 395 | 140
28 | 395 | 141
29 | 460 | 147
30 | 490 | 148
31 | 425 | 133
AVERAGE | 395.5714 | 141.4516
MAX | 490 | 151
MIN | 330 | 130

## Apr-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
EFFLUENT HARDNESS / MG/L
April | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 340 | 134
2 | 340 | 146
3 | 360 | 143
4 | 370 | 143
5 | 380 | 144
6 | 380 | 141
7 | 380 | 139
8 | 373 | 143
9 | 347 | 136
10 | 368 | 142
11 | 348 | 142
12 | 356 | 140
13 | 380 | 145
14 | 387 | 140
15 | 391 | 138
16 | 422 | 147
17 | 413 | 140
18 | 424 | 140
19 | 420 | 142
20 | 420 | 140
21 | 424 | 138
22 | 420 | 141
23 | 418 | 138
24 | 425 | 141
25 | 428 | 142
26 | 420 | 145
27 | 395 | 143
28 | 400 | 148
29 | 390 | 141
30 | 400 | 146
AVERAGE | 390.6333 | 141.6
MAX | 428 | 148
MIN | 340 | 134

## May-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
May | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 410 | 152 | settle tank out of service for cleaning
2 | 440 | 148 | settle tank out of service for cleaning
3 | 470 | 151 | settle tank out of service for cleaning
4 | 459 | 144 | settle tank out of service for cleaning
5 | 435 | 145 | settle tank out of service for cleaning
6 | 414 | 147 | settle tank out of service for cleaning
7 | 411 | 147 | settle tank out of service for cleaning
8 | 410 | 151 | settle tank out of service for cleaning
9 | 410 | 146
10 | 390 | 143
11 | 412 | 144
12 | 446 | 137
13 | 430 | 141
14 | 433 | 145
15 | 388 | 135
16 | 380 | 136
17 | 386 | 142
18 | 390 | 138
19 | 392 | 136
20 | 420 | 144
21 | 422 | 144
22 | 406 | 140
23 | 396 | 135
24 | 400 | 139
25 | 390 | 143
26 | 385 | 137
27 | 385 | 141
28 | 465 | 141
29 | 500 | 145
30 | 440 | 143
31 | 419 | 139
AVERAGE | 417.2258 | 142.5484
MAX | 500 | 152
MIN | 380 | 135

## June-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
June | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 495 | 148
2 | 475 | 149
3 | 464 | 133
4 | 427 | 126
5 | 505 | 135
6 | 450 | 138
7 | 414 | 140
8 | 383 | 134
9 | 392 | 135
10 | 396 | 147
11 | 378 | 144
12 | 410 | 147
13 | 463 | 149
14 | 410 | 142
15 | 346 | 136
16 | 328 | 138
17 | 333 | 140
18 | 340 | 144
19 | 340 | 143
20 | 350 | 136
21 | 350 | 141
22 | 335 | 140
23 | 360 | 144
24 | 395 | 148
25 | 420 | 146
26 | 400 | 139
27 | 400 | 135
28 | 417 | 137
29 | 403 | 140
30 | 377 | 137
AVERAGE | 398.5333 | 140.3667
MAX | 505 | 149
MIN | 328 | 126

## July-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
July | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 387 | 138
2 | 402 | 141
3 | 403 | 141
4 | 417 | 147
5 | 406 | 139
6 | 440 | 146
7 | 438 | 136
8 | 438 | 136
9 | 433 | 146
10 | 378 | 132
11 | 371 | 139
12 | 355 | 142
13 | 362 | 142
14 | 376 | 144
15 | 352 | 144
16 | 380 | 142
17 | 392 | 144
18 | 399 | 145
19 | 384 | 140
20 | 370 | 135
21 | 400 | 144
22 | 400 | 148
23 | 400 | 146
24 | 355 | 139
25 | 360 | 141
26 | 328 | 138
27 | 351 | 139
28 | 352 | 141
29 | 357 | 147
30 | 370 | 142
31 | 388 | 146
AVERAGE | 385.2903 | 141.6129
MAX | 440 | 148
MIN | 328 | 132

## Aug-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
August | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 408 | 145
2 | 412 | 142
3 | 418 | 140
4 | 408 | 140
5 | 405 | 139
6 | 430 | 145
7 | 423 | 144
8 | 400 | 140
9 | 400 | 143
10 | 400 | 142
11 | 412 | 142
12 | 420 | 146
13 | 435 | 143
14 | 433 | 145
15 | 424 | 140
16 | 420 | 142
17 | 418 | 145
18 | 398 | 142
19 | 390 | 140
20 | 395 | 143
21 | 415 | 144
22 | 410 | 142
23 | 393 | 134
24 | 370 | 126
25 | 374 | 135
26 | 395 | 145
27 | 428 | 148
28 | 420 | 141
29 | 414 | 140
30 | 420 | 142
31 | 432 | 140
AVERAGE | 410.3226 | 141.4516
MAX | 435 | 148
MIN | 370 | 126

## Sept-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
September | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 439 | 136
2 | 458 | 134
3 | 464 | 143
4 | 507 | 149
5 | 473 | 141
6 | 466 | 134
7 | 472 | 130
8 | 482 | 138
9 | 474 | 136
10 | 466 | 132
11 | 460 | 134
12 | 459 | 144
13 | 471 | 139
14 | 542 | 148
15 | 564 | 140
16 | 546 | 147
17 | 516 | 149
18 | 510 | 153 | High hardness level due to increased ground water pumpage do to low river levels
19 | 510 | 156 | and by-passing tank due to replacing tank flumes and isolation gates
20 | 500 | 150 | Estimated cost for flumes & gate replacement project $800K
21 | 500 | 150
22 | 500 | 159
23 | 540 | 186
24 | 540 | 175
25 | 540 | 169
26 | 540 | 177
27 | 548 | 171
28 | 524 | 157
29 | 498 | 180
30 | 474 | 195
AVERAGE | 499.4333 | 151.7333
MAX | 564 | 195
MIN | 439 | 130

## Oct-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
October | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 459 | 179 | High hardness level due to increased ground water pumpage, low river levels
2 | 499 | 198 | and by-passing tanks due to replacing tank flumes and isolation gates
3 | 499 | 161 | Estimated cost for flumes & gate replacement project $800K
4 | 482 | 178
5 | 485 | 184
6 | 510 | 166
7 | 529 | 168
8 | 528 | 154
9 | 525 | 154
10 | 520 | 158
11 | 516 | 148
12 | 527 | 150
13 | 538 | 157
14 | 530 | 151
15 | 530 | 152
16 | 530 | 152
17 | 530 | 150
18 | 526 | 152
19 | 498 | 158
20 | 500 | 156
21 | 500 | 156
22 | 500 | 165
23 | 482 | 149
24 | 500 | 160
25 | 520 | 164
26 | 507 | 149
27 | 489 | 156
28 | 490 | 168
29 | 511 | 188
30 | 496 | 159
31 | 483 | 167
AVERAGE | 507.7097 | 161.5161
MAX | 538 | 198
MIN | 459 | 148

## Nov-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
November | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L | High hardness level do to replacing tank flumes & isolation gates. Estimated cost of project $800,000
1 | 494 | 176 | Settle tank out of service
2 | 482 | 182 | Settle tank out of service
3 | 470 | 180 | Settle tank out of service
4 | 462 | 176 | Settle tank out of service
5 | 498 | 180 | Settle tank out of service
6 | 500 | 176 | Settle tank out of service
7 | 498 | 188 | Settle tank out of service
8 | 509 | 187 | Settle tank out of service
9 | 518 | 198 | Mix tank #1 & clarifier out of service
10 | 515 | 179 | Mix tank #1 & clarifier out of service
11 | 517 | 193 | Mix tank #1 & clarifier out of service
12 | 503 | 193 | Mix tank #1 & clarifier out of service
13 | 507 | 188 | Mix tank #1 & clarifier out of service
14 | 510 | 194 | Mix tank #1 & clarifier out of service
15 | 510 | 190 | Mix tank #1 & clarifier out of service
16 | 500 | 205 | Mix tank #1 & clarifier out of service
17 | 490 | 180 | Mix tank #1 & clarifier out of service
18 | 490 | 194 | Mix tank #1 & clarifier out of service
19 | 470 | 192 | Mix tank #1 & clarifier out of service
20 | 475 | 195 | Mix tank #1 & clarifier out of service
21 | 460 | 203 | Mix tank #1 & clarifier out of service
22 | 505 | 209 | Mix tank #1 & clarifier out of service
23 | 518 | 181 | Mix tank #1 & clarifier out of service
24 | 473 | 182 | Mix tank #1 & clarifier out of service
25 | 495 | 187 | Mix tank #1 & clarifier out of service
26 | 493 | 187 | Mix tank #1 & clarifier out of service
27 | 510 | 194 | Mix tank #1 & clarifier out of service
28 | 485 | 191 | Mix tank #1 & clarifier out of service
29 | 450 | 188 | Mix tank #1 & clarifier out of service
30 | 432 | 174 | Mix tank #1 & clarifier out of service
AVERAGE | 491.3 | 188.0667
MAX | 518 | 209
MIN | 432 | 174

## Dec-10
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2010
MARION EFFLUENT HARDNESS / MG/L
December | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L | High hardness level do to replacing tank flumes & isolation gates. Estimated cost of project $800,000
1 | 484 | 182 | Mix tank #1 & clarifier out of service
2 | 510 | 188 | Mix tank #1 & clarifier out of service
3 | 490 | 180 | Mix tank #1 & clarifier out of service
4 | 464 | 180 | Mix tank #1 & clarifier out of service
5 | 432 | 182 | Mix tank #1 & clarifier out of service
6 | 424 | 172 | Mix tank #1 & clarifier out of service
7 | 440 | 192 | Mix tank #1 & clarifier out of service
8 | 438 | 200 | Mix tank #1 & clarifier out of service
9 | 440 | 199 | Mix tank #1 & clarifier out of service
10 | 438 | 185 | Mix tank #1 & clarifier out of service
11 | 430 | 190 | Mix tank #1 & clarifier out of service
12 | 432 | 191 | Mix tank #1 & clarifier out of service
13 | 428 | 191 | Mix tank #1 & clarifier out of service
14 | 430 | 174 | Mix tank #1 out of service
15 | 410 | 150 | Mix tank #2 out of service
16 | 420 | 164 | Mix tank #2 out of service
17 | 420 | 157 | Mix tank #2 out of service
18 | 430 | 151 | Mix tank #2 out of service
19 | 444 | 151 | Mix tank #2 out of service
20 | 452 | 155 | Mix tank #2 out of service
21 | 450 | 156 | Mix tank #2 out of service
22 | 454 | 147 | Mix tank #2 out of service
23 | 461 | 134
24 | 440 | 138
25 | 440 | 150
26 | 444 | 154 | Recarb tank out of service
27 | 446 | 154 | Recarb tank out of service
28 | 486 | 153 | Recarb tank out of service
29 | 506 | 152 | ALL TANKS BACK IN SERVICE @ 16:00
30 | 470 | 140
31 | 450 | 140
AVERAGE | 448.4333 | 167.0667
MAX | 510 | 200
MIN | 410 | 134

## Jan-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
January | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 436 | 140
2 | 452 | 148
3 | 464 | 154
4 | 445 | 150
5 | 413 | 139
6 | 400 | 143
7 | 410 | 143
8 | 417 | 145
9 | 422 | 144
10 | 430 | 145
11 | 435 | 141
12 | 450 | 150
13 | 460 | 151
14 | 450 | 142
15 | 450 | 143
16 | 450 | 147
17 | 449 | 145
18 | 443 | 144
19 | 446 | 145
20 | 433 | 141
21 | 428 | 144
22 | 426 | 142
23 | 436 | 141
24 | 445 | 148
25 | 454 | 150
26 | 452 | 144
27 | 448 | 142
28 | 460 | 146
29 | 456 | 148
30 | 442 | 140
31 | 456 | 146
AVERAGE | 440.0667 | 144.8333
MAX | 464 | 154
MIN | 400 | 139

## Feb-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
February | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 460 | 151
2 | 448 | 135
3 | 457 | 140
4 | 490 | 149
5 | 490 | 144
6 | 478 | 140
7 | 470 | 144
8 | 456 | 139
9 | 450 | 144
10 | 480 | 152
11 | 480 | 151
12 | 490 | 145
13 | 490 | 144
14 | 475 | 146
15 | 418 | 134
16 | 400 | 140
17 | 405 | 146
18 | 456 | 143
19 | 466 | 143
20 | 408 | 143
21 | 410 | 146
22 | 410 | 148
23 | 390 | 144
24 | 380 | 148
25 | 380 | 148
26 | 380 | 146
27 | 390 | 144
28 | 470 | 148
AVERAGE | 442.0357 | 144.4643
MAX | 490 | 152
MIN | 380 | 134

## Mar-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
March | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 525 | 149
2 | 478 | 144
3 | 443 | 143
4 | 438 | 144
5 | 490 | 149
6 | 550 | 154 | heavy rains and runoff
7 | 540 | 148
8 | 490 | 144
9 | 480 | 142
10 | 500 | 148
11 | 470 | 143
12 | 460 | 147
13 | 440 | 143
14 | 413 | 141
15 | 406 | 139
16 | 398 | 147
17 | 366 | 140
18 | 355 | 139
19 | 361 | 143
20 | 359 | 148
21 | 350 | 144
22 | 360 | 146
23 | 360 | 142
24 | 380 | 143
25 | 370 | 143
26 | 365 | 142
27 | 365 | 141
28 | 373 | 141
29 | 365 | 141
30 | 369 | 144
31 | 378 | 142
AVERAGE | 419.2581 | 144
MAX | 550 | 154
MIN | 350 | 139

## Apr-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
April | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 370 | 140
2 | 370 | 139
3 | 370 | 142
4 | 386 | 144
5 | 498 | 159 | heavy rains and runoff
6 | 544 | 158 | heavy rains and runoff
7 | 448 | 133
8 | 412 | 144
9 | 380 | 142
10 | 373 | 143
11 | 370 | 139
12 | 370 | 148
13 | 370 | 148
14 | 370 | 142
15 | 370 | 143
16 | 370 | 143
17 | 362 | 146
18 | 374 | 149
19 | 370 | 146
20 | 420 | 149
21 | 480 | 148
22 | 490 | 146
23 | 450 | 140
24 | 450 | 142
25 | 453 | 146
26 | 517 | 152 | heavy rains and runoff
27 | 543 | 156 | heavy rains and runoff
28 | 480 | 149
29 | 420 | 143
30 | 389 | 143
AVERAGE | 418.9667 | 145.4
MAX | 544 | 159
MIN | 362 | 133

## May-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
May | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 330 | 141
2 | 400 | 144
3 | 500 | 150
4 | 500 | 146
5 | 452 | 146
6 | 394 | 142
7 | 388 | 146
8 | 358 | 144
9 | 320 | 145
10 | 323 | 147
11 | 337 | 147
12 | 357 | 147
13 | 495 | 155 | heavy rains and runoff
14 | 556 | 149
15 | 490 | 142
16 | 490 | 144
17 | 460 | 144
18 | 450 | 144
19 | 420 | 142
20 | 380 | 142
21 | 390 | 144
22 | 380 | 144
23 | 378 | 146
24 | 392 | 142
25 | 520 | 152 | heavy rains and runoff
26 | 553 | 149
27 | 573 | 142
28 | 583 | 145
29 | 502 | 145
30 | 465 | 140
31 | 453 | 142
AVERAGE | 438.3548 | 145.0968
MAX | 583 | 155
MIN | 320 | 140

## June-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
June | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 406 | 136
2 | 384 | 138
3 | 370 | 143
4 | 363 | 145
5 | 373 | 144
6 | 419 | 151
7 | 448 | 144
8 | 440 | 135
9 | 426 | 138
10 | 430 | 147
11 | 503 | 143
12 | 543 | 156 | heavy rains and runoff
13 | 474 | 142
14 | 448 | 148
15 | 408 | 142
16 | 396 | 144
17 | 394 | 144
18 | 388 | 142
19 | 410 | 142
20 | 430 | 145
21 | 420 | 147
22 | 420 | 145
23 | 400 | 144
24 | 400 | 139
25 | 400 | 142
26 | 400 | 140
27 | 404 | 145
28 | 418 | 145
29 | 428 | 147
30 | 429 | 142
AVERAGE | 419.0667 | 143.5
MAX | 543 | 156
MIN | 363 | 135

## July-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
July | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 430 | 140
2 | 448 | 140
3 | 484 | 143
4 | 479 | 146
5 | 431 | 131
6 | 381 | 137
7 | 386 | 140
8 | 398 | 150
9 | 403 | 159 | 2 MG Settle Tank out of service for cleaning
10 | 409 | 154 | 2 MG Settle Tank out of service for cleaning
11 | 412 | 148 | 2 MG Settle Tank out of service for cleaning
12 | 442 | 154 | 2 MG Settle Tank out of service for cleaning
13 | 414 | 146 | 2 MG Settle Tank out of service for cleaning
14 | 418 | 149 | 2 MG Settle Tank out of service for cleaning
15 | 426 | 152 | 2 MG Settle Tank out of service for cleaning
16 | 440 | 154 | 2 MG Settle Tank out of service for cleaning
17 | 440 | 146 | 2 MG Settle Tank out of service for cleaning
18 | 450 | 150 | 2 MG Settle Tank out of service for cleaning
19 | 470 | 148 | 2 MG Settle Tank out of service for cleaning
20 | 450 | 147 | 2 MG Settle Tank out of service for cleaning
21 | 400 | 144 | 2 MG Settle Tank out of service for cleaning
22 | 420 | 152 | 2 MG Settle Tank out of service for cleaning
23 | 420 | 150 | 2 MG Settle Tank out of service for cleaning
24 | 520 | 161 | 2 MG Settle Tank out of service for cleaning
25 | 433 | 146 | 2 MG Settle Tank out of service for cleaning
26 | 390 | 148 | 2 MG Settle Tank out of service for inspection
27 | 400 | 158 | 2 MG Settle Tank out of service for inspection
28 | 400 | 153 | 2 MG Settle Tank out of service for inspection
29 | 414 | 160 | Filling Settle Tank
30 | 420 | 160 | Filling Settle Tank
31 | 433 | 160 | Filling Settle Tank
AVERAGE | 427.7742 | 149.2258
MAX | 520 | 161
MIN | 381 | 131

## Aug-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
August | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 427 | 147 | 2 MG Settle Tank back in service
2 | 424 | 138
3 | 418 | 139
4 | 393 | 138
5 | 374 | 141
6 | 398 | 135
7 | 410 | 149
8 | 392 | 144
9 | 420 | 142
10 | 408 | 142
11 | 398 | 138
12 | 392 | 138
13 | 396 | 140
14 | 386 | 140
15 | 390 | 134
16 | 410 | 141
17 | 410 | 145
18 | 410 | 143
19 | 390 | 136
20 | 390 | 139
21 | 400 | 144
22 | 414 | 148
23 | 427 | 139
24 | 420 | 140
25 | 374 | 142
26 | 343 | 140
27 | 358 | 140
28 | 377 | 145
29 | 398 | 147
30 | 408 | 147
31 | 412 | 144
AVERAGE | 398.9355 | 141.4516
MAX | 427 | 149
MIN | 343 | 134

## Sept-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
September | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 416 | 133
2 | 422 | 132
3 | 430 | 141
4 | 460 | 142
5 | 452 | 148
6 | 398 | 134
7 | 386 | 138
8 | 374 | 140
9 | 386 | 142
10 | 370 | 142
11 | 414 | 146
12 | 430 | 142
13 | 420 | 143
14 | 410 | 137
15 | 420 | 142
16 | 410 | 142 | 2 MG Clarifier out of service for cleaning and inspection
17 | 400 | 154 | 2 MG Clarifier out of service for cleaning and inspection
18 | 400 | 152 | 2 MG Clarifier out of service for cleaning and inspection
19 | 427 | 163 | 2 MG Clarifier out of service for cleaning and inspection
20 | 430 | 164 | 2 MG Clarifier out of service for cleaning and inspection
21 | 424 | 151 | 2 MG Clarifier out of service for cleaning and inspection
22 | 395 | 149 | 2 MG Clarifier out of service for cleaning and inspection
23 | 378 | 152 | 2 MG Clarifier out of service for cleaning and inspection
24 | 397 | 159 | 2 MG Clarifier out of service for cleaning and inspection
25 | 398 | 157 | 2 MG Clarifier out of service for cleaning and inspection
26 | 386 | 144 | 2 MG Clarifier back in service
27 | 369 | 140
28 | 395 | 144
29 | 405 | 145
30 | 416 | 144
AVERAGE | 407.2667 | 145.4
MAX | 460 | 164
MIN | 369 | 132

## Oct-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
October | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 427 | 149
2 | 429 | 152
3 | 410 | 144
4 | 424 | 148
5 | 394 | 149
6 | 406 | 142
7 | 408 | 146
8 | 416 | 144
9 | 428 | 146
10 | 435 | 143
11 | 451 | 147
12 | 440 | 148
13 | 430 | 126
14 | 420 | 144 | 2 MG Settle Tank Out of Service for Cleaning
15 | 420 | 153 | 2 MG Settle Tank Out of Service for Cleaning
16 | 420 | 159 | 2 MG Settle Tank Out of Service for Cleaning
17 | 420 | 155 | 2 MG Settle Tank Out of Service for Cleaning
18 | 420 | 159 | 2 MG Settle Tank Out of Service for Cleaning
19 | 426 | 163 | 2 MG Settle Tank Out of Service for Cleaning
20 | 360 | 163 | 2 MG Settle Tank Out of Service for Cleaning
21 | 371 | 156 | 2 MG Settle Tank Out of Service for Cleaning
22 | 385 | 152
23 | 368 | 146
24 | 347 | 149
25 | 337 | 141
26 | 336 | 143
27 | 344 | 149
28 | 370 | 154
29 | 370 | 143
30 | 392 | 151
31 | 384 | 150
AVERAGE | 399.6129 | 148.8387
MAX | 451 | 163
MIN | 336 | 126

## Nov-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
November | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 382 | 138
2 | 366 | 142
3 | 372 | 138
4 | 374 | 146
5 | 370 | 140
6 | 376 | 144
7 | 400 | 146
8 | 410 | 143
9 | 420 | 140
10 | 420 | 137
11 | 420 | 137
12 | 430 | 147
13 | 470 | 147
14 | 428 | 136
15 | 454 | 147
16 | 448 | 137
17 | 398 | 145
18 | 398 | 152
19 | 364 | 145
20 | 353 | 145
21 | 360 | 149
22 | 388 | 145
23 | 439 | 152
24 | 437 | 142
25 | 456 | 145
26 | 453 | 149
27 | 450 | 150
28 | 414 | 148
29 | 398 | 142
30 | 436 | 148
AVERAGE | 409.4667 | 144.0667
MAX | 470 | 152
MIN | 353 | 136

## Dec-11
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2011
MARION EFFLUENT HARDNESS / MG/L
December | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 426 | 144
2 | 390 | 138
3 | 380 | 142
4 | 362 | 142
5 | 420 | 150
6 | 460 | 151
7 | 450 | 148
8 | 430 | 146
9 | 360 | 143
10 | 360 | 144
11 | 360 | 152
12 | 360 | 150
13 | 370 | 150
14 | 377 | 155
15 | 399 | 143
16 | 468 | 149
17 | 436 | 148
18 | 430 | 143
19 | 498 | 151
20 | 464 | 133
21 | 475 | 138
22 | 502 | 141
23 | 471 | 145
24 | 457 | 140
25 | 443 | 148
26 | 410 | 140
27 | 382 | 136
28 | 356 | 142
29 | 378 | 148
30 | 396 | 146
31 | 434 | 142
AVERAGE | 416.2581 | 144.7742
MAX | 502 | 155
MIN | 356 | 133

## Jan-12
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2012
MARION EFFLUENT HARDNESS / MG/L
January | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 482 | 149
2 | 420 | 141
3 | 400 | 146
4 | 420 | 150
5 | 400 | 136
6 | 400 | 144
7 | 410 | 145
8 | 410 | 146
9 | 403 | 143
10 | 406 | 141
11 | 400 | 140
12 | 392 | 140
13 | 416 | 149
14 | 417 | 148
15 | 425 | 151
16 | 403 | 143
17 | 388 | 146
18 | 426 | 148
19 | 451 | 148
20 | 428 | 142
21 | 418 | 144
22 | 423 | 142
23 | 418 | 140
24 | 448 | 142
25 | 420 | 148
26 | 432 | 146
27 | 488 | 149
28 | 476 | 144
29 | 496 | 140
30 | 450 | 145
31 | 410 | 141
AVERAGE | 425.0323 | 144.4194
MAX | 496 | 151
MIN | 388 | 136

## Feb-12
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2012
MARION EFFLUENT HARDNESS / MG/L
February | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 380 | 145
2 | 360 | 144
3 | 350 | 142
4 | 360 | 148
5 | 380 | 157 | slaker stopped no audible alarm, has been repaired
6 | 393 | 151
7 | 384 | 149
8 | 366 | 137
9 | 353 | 138
10 | 359 | 143
11 | 380 | 143
12 | 416 | 150
13 | 426 | 143
14 | 408 | 140
15 | 392 | 136
16 | 380 | 134
17 | 397 | 141
18 | 406 | 151
19 | 399 | 149
20 | 376 | 144
21 | 360 | 140
22 | 368 | 140
23 | 370 | 142
24 | 374 | 138
25 | 430 | 144
26 | 434 | 146
27 | 420 | 145
28 | 380 | 140
29 | 430 | 147
AVERAGE | 387.2759 | 143.6897
MAX | 434 | 157
MIN | 350 | 134

## Mar-12
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2012
MARION EFFLUENT HARDNESS / MG/L
March | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 530 | 152
2 | 540 | 141
3 | 560 | 143
4 | 540 | 150
5 | 512 | 144
6 | 451 | 144
7 | 378 | 146
8 | 345 | 146
9 | 347 | 145
10 | 340 | 148
11 | 340 | 147
12 | 349 | 145
13 | 360 | 143
14 | 352 | 141
15 | 337 | 139
16 | 387 | 145
17 | 360 | 140
18 | 350 | 140
19 | 344 | 142
20 | 408 | 144
21 | 464 | 148
22 | 446 | 142
23 | 394 | 140
24 | 370 | 136
25 | 360 | 146
26 | 370 | 145
27 | 360 | 140
28 | 370 | 141
29 | 370 | 141
30 | 370 | 144
31 | 380 | 143
AVERAGE | 399.4839 | 143.5806
MAX | 560 | 152
MIN | 337 | 136

## Apr-12
OHIO AMERICAN WATER COMPANY
MARION - DISTRICT |  |  | 2012
MARION EFFLUENT HARDNESS / MG/L
April | RAW HARDNESS MG/L | EFFLUENT HARDNESS MG/L
1 | 380 | 147
2 | 370 | 141
3 | 370 | 140
4 | 371 | 143
5 | 372 | 144
6 | 363 | 144
7 | 357 | 142
8 | 376 | 140
9 | 406 | 139
10 | 406 | 140
11 | 404 | 143
12 | 407 | 145
13 | 412 | 144
14 | 401 | 142
15 | 403 | 144
16 | 378 | 142
17 | 360 | 140
18 | 360 | 144
19 | 370 | 146
20 | 378 | 146
21 | 396 | 144
22 | 386 | 144
23 | 370 | 141
24 | 420 | 149
25 | 420 | 140
26 | 390 | 138
27 | 370 | 140
28 | 340 | 143
29 | 370 | 150
30 | 367 | 148
AVERAGE | 382.4333 | 143.1
MAX | 420 | 150
MIN | 340 | 138