## Exhibit A - Summary
Summary of Energy Savings from Transmission and Distribution Projects |  |  |  |  | Exhibit A
Projects placed in service 2010 (a)
Case No. TBD
(in MWhs)
| OE | CEI | TE | Total
Transmission System Annualized Energy Savings (b) | 2641.248 | 745.908 | 688.844 | 4076
Distribution System Annualized Energy Savings | 363 | 139 | 1946 | 2448
Total Energy Savings | 3004.248 | 884.908 | 2634.844 | 6524
(a) For Transmission project listing, see Exhibit C; for Distribution project listing, see Exhibit D
(b) Allocation of transmission energy savings is based on transmission line miles within each operating company compared to total FirstEnergy (Ohio) transmission line miles
| OE | CEI | TE
Loss Allocation % | 64.8% | 18.3% | 16.9%

## Exhibit C-Transmission Projects
FE-Ohio Transmission Level Projects | [7 empty] | Exhibit C
Based on new transmission facilities placed in service 2010.
Case No. TBD
| A | B | C | D | E | F | G
| (column descriptions below) |  |  |  |  | (D - E)
|  |  |  | FE-Ohio | FE-Ohio |  | 2010
|  |  | Actual/Projected | Total | Total | 2010 | Annualized
|  | Pri | In Service | Losses | Losses | MW Loss | MWH Loss
| Project Name | kV | Date | (Before) | (After) | Reduction | Reduction
| Lakeview 34.5 kV Cap Bank (18.9 MVAR) | 34.5 | 2010-01-04 | 405 | 404.8 | 0.2 | 741.096
| New 138 kV delivery point to Cleveland Public Power | 138 | 2010-07-12 | 405.7 | 404.8 | 0.9 | 3334.932
[5 empty] | Total | 1.1 | 4076.028
Column Description
A | Project description
B | Primary voltage
C | Date project was put into service
D | FE-Total Losses Before - system modeled using PSLF software prior to project completion. For a description of the system, see
http://www.gepower.com/prod_serv/products/utility_software/en/ge_pslf/index.htm
E | FE-Total Losses After - system modeled using PSLF software after project completion
F | MW Loss Reduction (column D - column E)
G | Calculation of MWhs
Formula: MW Loss Reduction x Average Loss Factor x 8760

## Exhibit D1- OE Projects
Ohio Edison Distribution Level Projects
Based on new distribution facilities placed in service 2010. |  |  |  |  | Exhibit D
Case No. TBD |  |  |  |  | (1 of 3)
| A | B | C | D
| (column descriptions below) |  |  | 2010
Annualized
|  | Actual/Projected | 2010 Peak | Loss
|  | In Service | Loss Reduction | Reduction
| Project Name | Date | MW | MWhs
| Reconductor line along North St. | 2010-07-12 | 0.018 | 49
| Jefferson Sub - R/P Transformer #2 | 2010-10-26 | 0.01 | 27
| Capacitors - OE Distr. Additions - 2010 | 2010-06-01 | 0.11 | 287
| Total 2010 Loss Reductions - Distribution Projects |  | 0.138 | 363
Column Description
A | Project description
B | Date project was put into service
C | MW Loss Reduction - Losses Before minus Losses After modeled in Millsoft engineering software. For a description, see
https://milsoft.com/smart-grid/windmill/analysis-funcitons
D | Calculation of MWhs
Formula: MW Loss Reduction x Average Loss Factor x 8760
Loss Factor = 31.2%; derivation based on annual calculation of load factor and associated loss factor.
(a) As explained in the Application, loss reductions were based on a 2kW loss per 100 kVAR. The MWh conversion is
as described in (D) above.

## Exhibit D2 -TE Projects
Toledo Edison Distribution Level Projects
Based on new distribution facilities placed in service 2010. |  |  |  |  | Exhibit D
Case No. TBD |  |  |  |  | (2 of 3)
| A | B | C | D
2010
Annualized
|  | Actual/Projected | 2010 Peak | Loss
|  | In Service | Loss Reduction | Reduction
| Project Name | Date | MW | MWhs
| Weston Sub - Replace #2 Transformer | 2010-05-26 | 0.165 | 451
| St. Charles Hospital - New Substation | 2010-09-29 | 0.06 | 164
| Replace Transformers Program 2010 | 2010-12-31 | 0.181 | 495
| Capacitors - TE Distribution Additions - 2010 | 2010-06-01 | 0.31 | 836
| Total 2010 Loss Reductions - Distribution Projects |  | 0.716 | 1946
Column Description
A | Project description
B | Date project was put into service
C | MW Loss Reduction - Losses Before minus Losses After modelled in Millsoft engineering software.
D | Calculation of MWhs
Formula: MW Loss Reduction x Average Loss Factor x 8760
Loss Factor = 31.2%; derivation based on annual calculation of load factor and associated loss factor.
(a) As explained in the Application, loss reductions were based on a 2kW loss per 100 kVAR. The MWh conversion is
as described in (D) above.

## Exhibit D3 CEI Projects
CEI Distribution Level Projects
Based on new distribution facilities placed in service 2010. |  |  |  |  | Exhibit D
Case No. TBD |  |  |  |  | (3 of 3)
| A | B | C | D
2010
Annualized
|  | Actual/Projected | 2010 Peak | Loss
|  | In Service | Loss Reduction | Reduction
| Project Name | Date | MW | MWhs
| Clifford Line Reconductor (Bagley Rd.) | 2010-07-20 | 0.051 | 139
| Total 2010 Loss Reductions - Distribution Projects |  | 0.051 | 139
Column Description
A | Project description
B | Date project was put into service
C | MW Loss Reduction - Losses Before minus Losses After modelled in Millsoft engineering software.
D | Calculation of MWhs
Formula: MW Loss Reduction x Average Loss Factor x 8760
Loss Factor = 31.2%; derivation based on annual calculation of load factor and associated loss factor.
(a) | Capacitor projects included in this exhibit are not the same as those included on page 1 and 2 of Exhibit E.
Capacitor additions are calculated in two methods. For substation located (single location) capacitor banks,
the same calculation applicable for distribution projects is applicable.