Case No.:  09-526-EL-REN

Name of Renewable Generating Facility:   Schmack BioMass - OARDC

The name specified will appear on the facility’s certificate of eligibility issued by the Public Utilities Commission of Ohio.

Facility Location:

Street Address:  2700 Selby Road

City:  Wooster    State:  Ohio    Zip Code:  44691

Facility Latitude and Longitude

Latitude:  40.7705	Longitude:  -81.9109

There are internet mapping tools available to determine your latitude and longitude, if you do not have this information.

If applicable, U.S. Department of Energy, Energy Information Administration Form EIA-860 Plant Name and Plant Code.

EIA-860 Plant Name:

EIA Plant Code:

Name of the Facility Owner:  Schmack Biomass - OARDC, LLC

Please note that the facility owner name listed will be the name that appears on the certificate.

If the facility has multiple owners, please provide the following information for each on additional sheets.

Applicant’s Legal Name:  Schmack Biomass - OARDC, LLC

Title:

Organization:

Owner’s Address:  7624 Riverview Road

Street Address:

City:  Cleveland        State:  OH        Zip Code:  44141

Country:  USA

Phone:  216.986.9999      Fax:  216.986.9999      Email Address:  delias@schmackbioenergy.com

Web Site Address (if applicable):  http://oardc.schmackbiomass.com

List name, address, telephone number and web site address under which Applicant will do business in Ohio.

Applicant’s Legal Name:  Schmack Biomass - OARDC, LLC

Title:

Organization:

Please note that the company name will appear on the certificate

Owner’s Address:  7624 Riverview Road

The address provided in this section is where the certificate will be sent

Street Address:  7624 Riverview Road

City:  Cleveland      State:  OH      Zip Code:  44141

Country:  USA

Phone:  216.986.9999      Fax:  216.986.9999      Email Address:  delias@schmackbioenergy.com

Web Site Address (if applicable):

Name of Generation Facility Operating Company:  Schmack Biomass - OARDC, LLC

Legal Name of Contact Person:  Deboarh Elias

Title:  Manager

Organization:  Schmack Biomass - OARDC, LLC

Operator’s Address:  7624 Riverview Road

Street Address:  7624 Riverview Road

City:  Cleveland      State:  OH      Zip Code:  44141

Country:  USA

Phone:  216.986.9999      Fax:  216.986.9999      Email Address:  delias@schmackbioenergy.com

Web Site Address (if applicable):  http://oardc.schmackbiomass.com

Contact person for regulatory or emergency matters:

Legal Name of Contact Person:  Bruce Bailey

Title:  VP of Technical Affairs

Organization:  Schmack Biomass - OARDC, LLC

Operator’s Address:  7624 Riverview Road

Street Address:  7624 Riverview Road

City:  Cleveland      State:  Ohio      Zip Code:  44141

Country:  USA

Phone:  216.986.9999      Fax:  216.986.9999      Email Address:  bbailey@schmackbioenergy.com

Web Site Address (if applicable):  http://oardc.schmackbiomass.com

Certification Criteria 1: Deliverability of the Generation into Ohio

Ohio Revised Code (ORC) Sec. 4928.64(B)(3)

The facility must have an interconnection with an electric utility.

Check which of the following applies to your facility’s location:

_(_	The facility is located in Ohio.

__	The facility is located in a state geographically contiguous to Ohio (Indiana, Kentucky, Michigan, Pennsylvania, or West Virginia).

__	The facility is located in the following state:

If the renewable energy resource generation facility is not located in Ohio, Indiana, Kentucky, Michigan, Pennsylvania, or West Virginia,  you are required to submit a study by one of the regional transmission organizations (RTO) operating in Ohio, either PJM or Midwest ISO, demonstrating that the power from your facility is physically deliverable into the state of Ohio.  The study may be conducted by someone other than the RTO provided that the RTO approves the study.  This study must be appended to your application as an exhibit.

Certification Criteria 2: Qualified Resource or Technology

You should provide information for only one resource or technology on this application; please check and/or fill out only one of the sections below.  If you are applying for more than one resource or technology, you will need to complete a separate application for each resource or technology.

For the resource or technology you identify below, please provide a written description of your system.  Please indicate if the facility is a customer-owned renewable distributed generation system.  Please also include a detailed description of how the output of the facility is going to be measured and verified.  If the facility is behind-the-meter and grid connected, please describe the configuration of the meter and the meter type.  Please also attach digital photographs that depict an accurate characterization of your installed system.  Please indicate the date(s) the photographs were taken.  If you need additional sheets for the description of your system, please include those as an exhibit and clearly identify the subject matter in the heading.

See Attached Exhibit A

The Applicant is applying for certification in Ohio based on the following qualified resource or technology (Sec. 4928.01 O.R.C.):

__  SOLAR PHOTOVOLTAIC

Total PV Capacity (DC):

Total PV Capacity (AC):

Expected Capacity Factor:

Anticipated Annual output in kWh/yr:

Location of the PV array:    __ Roof    __ Ground    __ Other

PV Modules

Manufacturer:

Model and Rating:

# of Modules and/or size of the array:

__  SOLAR THERMAL

__  WIND

Total Nameplate Capacity (DC):             kW DC

Expected Capacity Factor:

Anticipated Annual Output in kWh/yr or MWh/yr:

Wind Generators

If your system includes multiple generators, please provide the following information for each unique generator you have in your system

Manufacturer:

Model Name and Number:

Generator Nameplate Capacity (kilowatts DC):

# of Generators:

Wind Hub Height (ft):

Wind Rotor Diameter (ft):

__	HYDROELECTRIC ("hydroelectric facility" means a hydroelectric generating facility that is located at a dam on a river, or on any water discharged to a river, that is within or bordering this state or within or bordering an adjoining state (Sec. 4928.01(35) O.R.C.)

Check each of the following to verify that your facility meets each of the statutory standards (Sec. 4928.01(35) O.R.C.):

__	(a) The facility provides for river flows that are not detrimental for fish, wildlife, and water quality, including seasonal flow fluctuations as defined by the applicable licensing agency for the facility.

__	(b) The facility demonstrates that it complies with the water quality standards of this state, which compliance may consist of certification under Section 401 of the "Clean Water Act of 1977," 91 Stat. 1598, 1599, 33 U.S.C. 1341, and demonstrates that it has not contributed to a finding by this state that the river has impaired water quality under Section 303(d) of the "Clean Water Act of 1977," 114 Stat. 870, 33 U.S.C. 1313.

__	(c) The facility complies with mandatory prescriptions regarding fish passage as required by the Federal Energy Regulatory Commission license issued for the project, regarding fish protection for riverine, anadromous, and catadromus fish.

__	(d) The facility complies with the recommendations of the Ohio Environmental Protection Agency and with the terms of its Federal Energy Regulatory Commission license regarding watershed protection, mitigation, or enhancement, to the extent of each agency's respective jurisdiction over the facility.

__	(e) The facility complies with provisions of the "Endangered Species Act of 1973," 87 Stat. 884, 16 U.S.C. 1531 to 1544, as amended.

__	(f) The facility does not harm cultural resources of the area. This can be shown through compliance with the terms of its Federal Energy Regulatory Commission license or, if the facility is not regulated by that commission, through development of a plan approved by the Ohio Historic Preservation Office, to the extent it has jurisdiction over the facility.

__	(g) The facility complies with the terms of its Federal Energy Regulatory Commission license or exemption that are related to recreational access, accommodation, and facilities or, if the facility is not regulated by that commission, the facility complies with similar requirements as are recommended by resource agencies, to the extent they have jurisdiction over the facility; and the facility provides access to water to the public without fee or charge.

__	(h) The facility is not recommended for removal by any federal agency or agency of any state, to the extent the particular agency has jurisdiction over the facility.

__	GEOTHERMAL

__	SOLID WASTE (as defined in ORC section 3734.01), electricity generation using fuel derived from solid wastes through fractionation, biological decomposition, or other process that does not principally involve combustion. (Sec. 4928.01(A)(35) O.R.C.)

Identify all fuel types used by the facility and respective proportions (show by the percent of heat input):

_(_	BIOMASS

Identify the fuel type used by the facility:  Biomethane/CNG

If co-firing an electric generating facility with a biomass energy resource, the proportion of fuel input attributable to the biomass energy resource shall dictate the proportion of electricity output from the facility that can be considered biomass energy.

List all fuel types used by the facility and respective proportions (show by the percent of heat input):  Biomethane 100%

Please attach the formula for computing the proportions of output per fuel type by MWh or kWh generated.  See Attached Exhibit B:  Plant Parameters Sheet Summary Report

__	FUEL CELL (any fuel cell used in the generation of electricity, including, but not limited to, a proton exchange membrane fuel cell, phosphoric acid fuel cell, molten carbonate fuel cell, or solid oxide fuel cell; Sec. 4928.01(35)(A) O.R.C.).

Identify all fuel types used by the facility and respective proportions:

__	STORAGE FACILITY

If using compressed air or pumped hydropower, the renewable energy resource used to impel the resource into the storage reservoir is (include resource type and facility name):

Certification Criteria 3: Placed in Service Date (Sec. 4928.64. (A)(1) O.R.C.)

The Renewable Energy Facility:

__  has a placed-in-service date before January 1, 1998;  (month/day/year):

__  has a placed-in-service date on or after January 1, 1998; (month/day/year):

__  has been modified or retrofitted on or after January 1, 1998; (month/day/year):

Please provide a detailed description of the modifications or retrofits made to the facility that rendered it eligible for consideration as a qualified renewable energy resource.  In your description, please include the date of initial operation and the date of modification or retrofit to use a qualified renewable resource.  Please include this description as an exhibit attached to your application filing and identify the subject matter in the heading of the exhibit.

_(_  Not yet online; projected in-service date (month/day/year): ):  11/01/2009

Is the renewable energy facility owner a mercantile customer?  No

ORC Sec. 4928.01 (19) "Mercantile customer" means a commercial or industrial customer if the electricity consumed is for nonresidential use and the customer consumes more than seven hundred thousand kilowatt hours per year or is part of a national account involving multiple facilities in one or more states.

_(_  No

__  Yes

Has the mercantile customer facility owner committed to integrate the resource under the provisions of 4901:1-39-06 O.A.C?

__  No

__  Yes

If yes, please attach a copy of your approved application as an exhibit to this filing.

Facility Information

The nameplate capacity of the entire facility in megawatts (MW):  .4

If applicable, what is the expected heat rate of resource used per kWh of net generation:

5515 BTU/kWh

Number of Generating Units:  1

| In-Service date of each unit | The nameplate capacity of each unit in megawatts (MW) | Projected Annual Generation | Expected Annual Capacity Factor % |
| --- | --- | --- | --- |
| Anticipated date: 11/01/2009 | 0.4 | 2,837,0210 kWh | 88% |

(To expand the number of rows if more units need to be reported, place your cursor in the bottom right cell and hit tab).

Regional Transmission Organization Information

In which Regional Transmission Organization area is your facility located:

__  Within Geographic Area of PJM Interconnection, L.L.C.

__  Within Geographic Area of Midwest ISO

_(_  Other (specify):  Net Meter

Are you a member of a regional transmission organization?

__  Yes; specify which one:

_(_  No; explain why you are not a member of a regional transmission organization:  Ohio State University Campus Net Metering

Balancing Authority operator or control area operator for the facility:

__  PJM

__  Midwest ISO

_(_  Other (specify):  Net Metering

Attribute Tracking System Information

Are you currently registered with an attribute tracking system:  __  Yes	_(_  No

In which attribute tracking system are you currently registered or in which do you intend to register (the tracking system you identify will be the system the PUCO contacts with your eligibility certification):

__  GATS

__  M-RETS

_(_  Other (specify):  Net Meter Ohio State University Wooster Campus, AEP is the current Provider

Enter the generation ID number you have been assigned by the tracking system:  None

If the generation ID number has not yet been assigned, you will need to provide this number to the PUCO within 15 days of your facility receiving this number from the tracking system).

Other State Certification

Is the facility certified by another state as an eligible generating resource to meet the renewable portfolio standards of that state?

__  Yes

_(_  No

If yes, for each state, provide the following information:

| Name of State | State Certification Agency | State Certification Number | Date Issued |
| --- | --- | --- | --- |

(To expand the number of rows if more units need to be reported, place your cursor in the bottom right cell and hit tab).

Type of Generating Facility

Please check all of the following that apply to your facility:

__	Utility Generating Facility:

__  Investor Owned Utility

__  Rural Electric Cooperative

__  Municipal System

__	Electric Services Company (competitive retail electric service provider)

__	Distributed Generation with a net metering and interconnection agreement with a utility.

Identify the utility:

__	Distributed Generation with both on-site use and wholesale sales.

Identify the utility with which the facility is interconnected:

__	Distributed Generation, interconnected without net metering.

Identify the utility with which the facility is interconnected:

Note:  if the facility does not yet have an interconnection agreement with a utility or transmission system operator, please note here the status of the application for such an agreement:

Currently in Negotiations

Meter Specifications

All facilities are required to measure output with a utility grade meter.  Please provide this information for each meter used in your system.This is to be determined per negotiated terms of the interconnect agreement.

Manufacturer:

Serial Number:

Type:

Date of Last Certification:

Attach a photograph of the meter with date image taken.  The meter reading must be clearly visible in the photograph.

Total kWh shown on meter at time of photograph:

The Public Utilities Commission of Ohio reserves the right to verify the accuracy of the data reported to the tracking system and to the PUCO.

I. Written Description of the System:

Process Description:  Schmack is constructing an ecoFARMsystem 550 anaerobic digestion facility that will create domestic green renewable energy from organic wastes. Since 1993, Schmack technology has solved waste management issues facing farmers, municipal waste water treatment plants, and food processing companies. The continuous mix, high solids anaerobic digestion technology is proven, reliable and advanced.  This will be one of the first agricultural units constructed in the U.S. using Schmack’s German technology that supports hundreds of systems worldwide.  The successful launch and demonstration of this system will assist with the creation of a new advanced energy industry based in Ohio.

This system will generate domestic green renewable energy from manure, energy crops and food waste that was previously unused or being hauled to landfills.  Instead, the system will accept and process the material to generate sustainable renewable energy, reduce harmful greenhouse gas emissions and produce valuable byproducts which include fertilizer and organic soil amendments.

Schmack’s Wooster facility will be processing dairy manure, energy crops, and food waste. The System will accept approximately 36.3 wet tons of biomass per day with a total solids content of approx 21.4% from different sources. All waste material will be delivered to the site by truck. Operating at this capacity, the plant will generate 3.59 MMBtu per hour (31,430 MMBtu per year) of biogas and convert 90% of the system potential to useable energy.

|  | MMBtu | mWh |
| --- | --- | --- |
| Total Gas Potential | 31,430 | 9,211 |
| Output - Electric | 11,000 | 3,224 |
| Output - Waste Heat | 17,286 | 5,066 |
| Gross Output | 28,286 | 8,290 |
| Efficiency W/O Load | 90% | 90% |
| Parasitic Load - Heat | -1,638 | -480 |
| Parasitic Load - Electric | -1,650 | -484 |
| System Usage | -3,288 | -964 |
| Net Output | 24,998 | 7,327 |
| Efficiency, NET | 80% | 80% |

Benefits of processing biomass using a F550:

- Highly Efficient System:  The F550 is more than 80% efficient.

- Takes waste and generates renewable energy and beneficial products.

- Reduces Volatile Solids:   Reduction is between 40% and 60%.

- Requires Minimal Real Estate:   Overall footprint of no more than 2 acres.

- Increases Facility Lifespan:  Systems are engineered to last 20 years.

- Reduces Odors:   Allowing us to be a “Good Neighbor” to the community.

- Stabilizes biomass so it can be sold off-site as a product.

- Increases nutrient management options by creating products that can be readily moved off farms and off watersheds.

Schmack will be constructing a renewable energy system that will produce (i) thermal energy and electricity, (ii) carbon offsets, (iii) liquid fertilizer, and (iv) valuable soil amendments from the processing of biomass. The system will be constructed in Wooster, Ohio and will consist of a Schmack designed anaerobic digester, and exclusive gas cleaning and upgrade equipment from Biogas Technologies Unlimited, LLC.

The F550 system can be divided into the following areas:

- Biomass Area – Delivery and Pre-Processing, Heating, Mixing

- Receiving Tank – Hydrolysis and Acidification

- Digester Tank – Mesophilic Fermentation

- Effluent Processing – Dewatering

- Gas Processing –Cleaning and Drying, Flare

- CHP – Generator

- System Operation – Monitoring SCADA

## Biomass Area - Delivery & Preprocessing:  Trucks delivering high solids biomass will unload directly into a 30 yard receiving hopper.  Augers in the receiving hopper will chop the material and mix it with dilution liquid before discharging the hopper contents to an open hopper, progressive cavity pump.  Material is then pumped through a macerator to further reduce biomass particle size. Pumps then transfer the biomass to the receiving tank.

Receiving Tank:  Liquid, in the forms of dewatered filtrate, digestate, water, or a combination of these will be mixed with the solids to provide the proper consistency for pumping.  Stones or other unwanted solid materials will be removed from the biomass.  The hopper is designed to completely discharge in approximately 45 minutes.

Trucks delivering liquid biomass will be connected to a pump and discharged directly to the Receiving Tank.  The liquid biomass will be pumped through a mechanism to filter out any unwanted solid material.  A 6,000 gallon tanker truck can be unloaded in approximately 20 minutes.

The Receiving Tank provides a hydraulic storage buffer in front of the Digester Tank, providing up to 3 days of storage.  Biomass is dosed from the biomass Receiving Tank to the Digester Tank.

The Receiving Tank is a 50,000 gallon insulated, bolted steel tank.  The tank has a 16 foot diameter and is approximately 32 feet tall.  A side-entry prop mixer prevents formation of layers of the material, ensuring a consistent mix for feeding.  The tank will have a gas tight steel roof.  A pipe will connect the head space in the tank with the Digester Tank gas storage to maintain equalized gas pressure in the system.  This has the added benefit of controlling odor from this tank.  This will also provide an area for displaced gas due to filling/discharging or temperature expansion of contained material.  Safe pressure levels are maintained by an over/under pressure relief valve mounted to the tank.

## Digester Tank:   The Digester Tank provides the hydraulic retention time (approximately 30 days) necessary to allow methanogenic bacteria to convert organic biomass into biogas.  The digestate is heated to maintain approximately 100°F (mesophilic) in the tank using an external heat exchanger heated by the combined heat and power unit (CHP).  Alternatively, a hot water boiler fueled by biogas can be used to provide heat.  The Digester Tank is an insulated, bolted, steel tank with a working volume of 500,000 gallons with a 60 foot diameter and is approximately 30 feet tall.  Side-entry prop mixers prevent layer formation of the material, ensuring a consistent mix for feeding.  The conditioned biomass from the Receiving Tank is fed into the tank at a turbulence zone created by the mixer to minimize the time required to obtain a complete mix.

Gas storage in the digester tank will be accomplished with a single membrane roof system.  The membrane is supported by biogas pressure.  The membrane inflates and deflates according to the amount of biogas in the system.  When biogas is not present (during commissioning), the membrane is supported by a column and cable system to keep it from contacting the biomass.  The cables also have a second function of supporting a net.  The net provides surface area for colonization of natural aerobic bacteria to convert hydrogen sulfide in the biogas to elemental sulfur and sulfates.  This elemental sulfur then drops into the Digester Tank and is removed with the solids in the tank.  A metered amount of air is added to the biogas with a blower to support biological desulfurization.  The air level is maintained at 1%-2%.

Safe pressure levels are maintained by an over/under pressure relief valve mounted to the tank.  This prevents excessive pressure or vacuum in the system.

Effluent Processing - Dewatering System:  The suspended solids in the digested material will be mechanically separated from the water in a dewatering system.  The cake solids after this step will be around 20%-25% total dry solids and will be utilized for beneficial use off-site as animal bedding, soil amendments, or compost

The effluent from the dewatering equipment will be field applied as a fertilizer; this certifiable fertilizer will offset much of the costs of traditional commercial fertilizers.

### Gas Cleaning System:  The biogas will be cleaned, separated and upgraded using technology provided by BTU LLC.  BTU will provide equipment to produce pipeline quality natural gas from biogas. This is a two stage process consisting of biogas scrubbing and dehydration.

The biogas generated by Schmack’s F550 system is a water saturated stream composed primarily of methane (approximately 60%) and carbon dioxide (approximately 40%) and other impurities such as hydrogen sulfide & siloxane.

In the first stage of the upgrading process, biogas is cleaned using a wet scrubbing technology where the gas flows upward through a packed wet scrubber as the scrubbing solution flows downward; removing carbon dioxide and hydrogen sulfide impurities.  Biogas is supplied into the gas upgrade system at low pressure in a controlled flow rate dictated by the biogas production.  Following the wet scrubbing process, clean methane (biomethane) exits the top of the scrubber and is dried using dessicant drying and is available for use in traditional natural gas devices.

The scrubbing solution is reclaimed by heating it in a reboiler which liberates the entrained gases from the solution. The gases are released to the atmosphere or sent to a flare in compliance with environmental regulations.  In addition, any particulates that may have formed in the solution (from siloxanes found in the incoming biomass) are filtered out in a particulate filter.

Should downstream compression, metering and pressure regulation systems be required, they will be defined by the end user and included in the plant; for instance if CNG is desired.

Excess gas and effluent from the gas cleaning process will be flared. The emergency flare system is designed to consume maximum capacity of the plant for safety reasons.

CHP Unit:  A CHP Unit will use the biomethane to produce electric power which will be used on site and sold to the local public utility through a net metering arrangement; anticipated power generation is 368kW. In the generation of electricity using an internal combustion engine, thermal energy is also created (water jacket in the engine and exhaust heat); this thermal energy will be used on-site. Excess gas produced will be burned in a closed flare. If necessary, desulfurization equipment will be used if the natural desulfurization in the digester tank is not adequate.  Through electrical generation and thermal recovery, the anticipated efficiency is 90%.

System Operation:  Remote Monitoring and Controls: The “brain” of the System is a SCADA (Supervisory Control and Data Acquisition) that controls all system functions. The SCADA system continuously monitors all process control parameters.  Operators can remotely access the entire control system via the internet.  The system can page service technicians in the case of critical system warning messages. Safety measures are put in place to meet federal, state and local regulations.

Indicate if the facility is a customer-owned renewable distributed generation system.

The facility is not a customer-owned renewable distributed generation system.

Include a detailed description of how the output of the facility is going to be measured and verified.

The output of the facility will be measured and verified using two meters associated with the generation equipment; one at the power pole (standard electric meter, except it runs backwards to measure the power going onto the lines) and one in the control panel.

If the facility is behind-the-meter and grid connected, please describe the configuration of the meter and the meter type.

The facility will not be grid connected.  Electricity produced by the F550 will be supplied directly to select OARDC buildings on the campus.

Attach digital photographs that depict an accurate characterization of your installed system.  Please indicate the date(s) the photographs were taken.

# Text boxes

1-31-2009

8-24-2007